Specification

E/One Sentry Advisor

Remote Monitoring

Panel Option

Data Package

OPTION ON SIMPLEX AND DUPLEX PROTECT PLUS PANELS – FULL DATA PACKAGE

(OPTIONAL) Wireless Cellular Based Communication Package – The E/One Sentry Advisor uses a cellular transmitter to communicate operating parameters, trouble conditions and high level alarm. Each panel shall be equipped with hardware that interfaces with the panel’s circuit board assembly to obtain historical operating data and current system status. This information shall then be transmitted to a host system that utilizes an interactive website interface for end users to access the information.

A secure user ID and password shall be used to provide access to the website. The website shall quickly identify sites that may be experiencing trouble and shall be able to generate reports including: running tallies of usage, flow rates, potential infiltration, predictive maintenance indicators and asset mapping/management. The website shall also provide a means to configure alerts corresponding to the various trouble conditions that can be sent to users via secure e-mail, SMS text, phone or an existing telemetry system. These alerts can be sent to any number of recipients.

Accessible data shall include:

- Pump Runtime

- Pump Cycles

- Min, Max, Avg. and Last Runtime

- Min, Max, Avg. Operating Voltage, Wattage and Amperage

- Trouble Events

  - High Level Alarm

  - Brownout (low voltage)

  - Overvoltage

  - Run Dry (low wattage)

  - Overpressure (high wattage)

  - Excessive Runtime

- Alarm Circuit Fault

- Watt meter Fault

- Watt based Flow Rate Data

- Loss of Duplex Communication (between pumps, duplex stations only)

The E/One Sentry Advisor shall be equipped with a battery that will allow one message to be sent out in the event of a power loss.

The communication package shall be a factory prewired unit within the panel enclosure including the compact cellular transmitter, power supply and antenna. Panels with this option must be within range of the associated cellular network.

Environment One Corporation

2773 Balltown Road

Niskayuna, New York 12309

www.eone.com

A Precision Castparts Company

LM000423 Rev A