Typical

Specifications

Uni-Lateral:

Stainless Steel

Forced Sewer Main

Service Lateral Kits

SDR HDPE Pipe

Stainless Steel & Engineered Thermoplastics

(Compression Fitting)

SPECIFICATION:

SERVICE LATERAL KIT WITH STAINLESS STEEL VALVES AND

ENGINEERED THERMOPLASTIC COMPRESSION FITTINGS

1.0	GENERAL

1.01	General Description: The MANUFACTURER shall furnish Uni-Lateral service lateral kits (exclusive of piping), each consisting of three (3) compression fittings, one (1) combination curb stop/check valve assembly and one (1) curb box. The curb stop/check valve assembly shall be 316 stainless steel and have a two-piece cast 316 stainless steel housing, creating a unilateral body. All plastic compression fittings are to be molded from polypropylene and shall be tested for resistance to aging, pressure rating, tensile strength, and flexural strength. All components shall incorporate compression fitting connections for easy, reliable installation of piping. The lateral kit shall be rated for 150 psi service. Lateral kits with pressure-tested combination curb stop/check valve assembly shall be provided by Environment One Corporation, Niskayuna, New York, or approved equal. E/One requires that an E/One Uni-Lateral assembly (E/One part number NB0184PXX or NC0193GXX) or E/One Redundant Check Valve (E/One part number PC0051GXX) be installed in the pipe lateral outside the home between the pump discharge and the street main on all installations.

1.02	Shop Drawings: After receipt of notice to proceed, the MANUFACTURER shall furnish an electronic set of shop drawings that details the equipment to be furnished, including dimensional data and materials of construction. The SPECIFYING ENGINEER shall promptly review this data and return two (2) copies as accepted, or with requested modifications. Upon receipt of accepted shop drawings, the MANUFACTURER shall proceed immediately with fabrication of the equipment.

1.03	Warranty: All merchandise is warranted to be free from defects in materials and factory workmanship.  Environment One shall provide, free of charge, new products in equal quantities for any that prove defective within two (2) years from date of shipment from the factory. The MANUFACTURER shall not be liable for any loss, damage, or injury, direct or consequential, arising out of the use of or the inability to use the product. Before using, the user shall determine the suitability of the product for his intended use and user assumes all risk and liability whatever in connection therewith. No claims for labor or consequential damage will be allowed. The foregoing may not be changed except by agreement signed by an officer of the MANUFACTURER.

2.0	PRODUCT

2.01	Engineered Thermoplastic Fittings: All plastic fitting components are to be in compliance with applicable ASTM standards.

All pipe connections shall be made using compression fitting connections including a Buna-N O-ring for sealing to the outside diameter of the pipe. A split-collet locking device shall be integrated into all pipe connection fittings to securely restrain the pipe from hydraulic pressure and external loading caused by shifting and settling.

2.02	Stainless Steel Uni-Lateral Curb Stop/Check Valve Assembly: The Uni-Lateral shall be pressure-tight in both directions. The ball valve actuator shall include position stop features at the fully opened and closed positions. The curb stop/check valve assembly shall be designed to withstand a working pressure of 235 psi.

The stainless steel check valve shall be integral with the curb stop valve. The check valve will provide a full-ported 1-1/4” passageway and shall introduce minimal friction loss at maximum rated flow. The flapper hinge design shall provide a maximum degree of freedom and ensure seating at low back pressure.

2.03	Curb Boxes: Curb boxes shall be constructed of ABS, conforming to ASTM-D 1788. Lid top casting shall be cast iron, conforming to ASTM A-48 Class 25, providing magnetic detectability, and be painted black. The lid shall have the word “sewer” cast into it. All components shall be inherently corrosion-resistant to ensure durability in the ground. Curb boxes shall provide height adjustment downward (shorter) from their nominal height.

2.04	High Density Polyethylene Pipe (supplied by others): Pipe shall be have a working pressure of 160 psi minimum and shall be classified SDR per ASTM D 3035.

2.05	Deviations: If a supplier chooses to submit a bid that does not meet all the requirements of this specification, the bid shall include a written description of the deviation with data that shows the magnitude of the deviation and the justification for the deviation from this specification. The decision to accept material deviating from this specification shall be the responsibility of the specifying engineer.

2.06	Certification: The owner or the specifying ENGINEER may request certified lab data to verify the physical properties of the pipe materials supplied under this specification or may take random samples and have them tested by an independent laboratory.

2.07	Rejection: Polyethylene pipe may be rejected for failure to meet any of the requirements of this specification.

2.08	Pipe Dimensions: The SDR (Standard Dimension Ratio) of the pipe supplied shall be as specified by the SPECIFYING ENGINEER. SDR 7, 9 and 11 fittings are available from the manufacturer. SIDR 7 fittings will not work with SDR pipe.

3.0	Execution

3.01	Factory Test: The Uni-Lateral shall be 100 percent hydrostatically tested to 150 psi in the factory.

3.02	Construction Practices: Pipe shall be stored on clean, level ground to prevent undue scratching or gouging of the pipe. If the pipe must be stacked for storage, such stacking should be in accordance with the pipe manufacturer’s recommendations.  The pipe should be handled in such a manner that it is not damaged by being dragged over sharp objects or cut by chokers or lifting equipment.

Segments of pipe having cuts or gouges in excess of 10 percent of the wall thickness of the pipe shall be cut out and removed. The undamaged portions of the pipe shall be rejoined using the butt fusion joining method. Sections of polyethylene pipe should be joined into continuous lengths on the job site above ground. The joining method shall be the butt-fusion method and shall be performed in strict accordance with the pipe manufacturer’s recommendations. The butt-fusion equipment used in the joining procedure shall be capable of meeting all conditions recommended by the pipe manufacturer, including, but not limited to, fusion temperature, alignment, and fusion pressure.

Fused segments of pipe shall be handled so as to avoid damage to the pipe. When lifting fused sections of pipe, chains or cable-type chokers should be avoided. Nylon slings are preferred. Spreader bars should be used when lifting long, fused sections. Care should be exercised to avoid cutting or gouging the pipe.

3.03	Installation:	Assemble the compression fittings according to the fitting manufacturer’s recommendations.

The trench and trench bottom should be constructed in accordance with ASTM D 2321. Embedment materials should be Class I, Class II or Class III materials as defined in ASTM D 2321. The use of Class IV and/or Class V materials for embedment is not recommended and should be allowed only with the approval of the SPECIFYING ENGINEER. Bedding of the pipe should be performed in accordance with ASTM D 2321. Compaction should be as specified in ASTM D 2321. Deviations from the specified compaction shall be approved by the SPECIFYING ENGINEER.

Haunching and initial backfill should be as specified in ASTM D 2321 using Class I, Class II or Class III materials. Materials used and compaction shall be as specified by the SPECIFYING ENGINEER. In cases where a compaction of 85 percent Standard Proctor Density is not attainable, the SPECIFYING ENGINEER may wish to increase the SDR of the pipe to provide adequate stiffness. ASTM D 2321 sections titled “Minimum Cover for Load Application,” “Use of Compaction Equipment” and “Removal of Trench Protection” should apply unless directed otherwise by the SPECIFYING ENGINEER.

END OF SECTION

Environment One

2773 Balltown Road

Niskayuna, New York 12309

NA0333P01 Rev B  7/17